## Maintenance History
BHARAT STEEL PLANT – MAINTENANCE HISTORY LOG
Equipment: Centrifugal Pumps PUMP-101 & PUMP-102 ¦ Location: Pump House B ¦ Period: Jan 2022 – Oct 2024
WO Number | Date | Equipment Tag | Type | Description | Technician | Supervisor | Parts Used | Downtime (hrs) | Cost (INR) | OISD-117 Ref. | Status
WO-2022-0110 | 10-Jan-2022 | PUMP-101 | PM | Annual overhaul: bearing replacement DE & NDE, seal inspection, alignment check, wearing ring measurement | Ramesh Kumar | Ajay Mehta | SKF-6309-2RS x1, SKF-6306-2RS x1, MSHC100-500G x1 | 8 | 9800 | Cl. 5.2, 6.1, 6.3 | CLOSED
WO-2022-0405 | 05-Apr-2022 | PUMP-102 | CM | Suction strainer choked – reduced flow. Strainer cleaned. No parts replaced. | Vikram Singh | Ajay Mehta | None | 2 | 500 | Cl. 5.1 | CLOSED
WO-2022-0918 | 18-Sep-2022 | PUMP-101 | PM | Quarterly inspection: vibration check, bearing temp check, seal check. All OK. Lubrication done. | Ramesh Kumar | S. Patil | MSHC100-500G x1 | 1 | 850 | Cl. 5.2, 6.1 | CLOSED
WO-2022-1201 | 01-Dec-2022 | PUMP-102 | PM | Quarterly inspection: vibration 2.1 mm/sec (within limit). Seal weeping minor – logged. Lubrication done. | Vikram Singh | Ajay Mehta | MSHC100-500G x1 | 1 | 850 | Cl. 5.2, 6.3 | CLOSED
WO-2023-0115 | 15-Jan-2023 | PUMP-101 | PM | Annual overhaul: bearings inspected (acceptable), seal inspected (good condition), alignment verified TIR 0.04mm. | Ramesh Kumar | Ajay Mehta | GKT-DN65-SW x2, MSHC100-500G x1 | 6 | 2950 | Cl. 5.2, 6.1, 6.3 | CLOSED
WO-2023-0320 | 20-Mar-2023 | PUMP-102 | CM | Coupling grid element cracked – abnormal noise. Grid coupling replaced. Alignment rechecked TIR 0.03mm. | Ramesh Kumar | Ajay Mehta | COUP-GRID-KBL x1 | 4 | 12000 | Cl. 7.4 | CLOSED
WO-2023-0601 | 01-Jun-2023 | PUMP-101 | PM | Quarterly inspection: vibration 2.3 mm/sec – slightly elevated. Bearing temp Amb+15°C – acceptable. Greased. | Vikram Singh | Ajay Mehta | MSHC100-500G x1 | 1 | 850 | Cl. 5.2, 6.1 | CLOSED
WO-2023-0622 | 22-Jun-2023 | PUMP-101 | CM | Vibration follow-up inspection after WO-2023-0601. Identified minor impeller wear. Impeller cleaned and balanced. | Ramesh Kumar | R.K. Sharma | None | 6 | 2000 | Cl. 5.2 | CLOSED
WO-2023-0915 | 15-Sep-2023 | PUMP-102 | PM | Quarterly inspection: all parameters normal. Vibration 1.9 mm/sec. Seal clean, no leakage. Lubrication done. | Vikram Singh | S. Patil | MSHC100-500G x1 | 1 | 850 | Cl. 5.2, 6.1, 6.3 | CLOSED
WO-2023-1210 | 10-Dec-2023 | PUMP-101 | PM | Annual PM: NDE bearing worn but acceptable (L10 remaining ~40%). Flagged for next PM replacement. Seal OK. | Ramesh Kumar | Ajay Mehta | GKT-DN65-SW x2, MSHC100-500G x1 | 5 | 2950 | Cl. 5.2, 6.1, 6.3 | CLOSED
WO-2024-0312 | 12-Mar-2024 | PUMP-101 | CM | DE bearing failed (pitting, cage fracture). Vibration: 6.2 mm/sec trigger. Bearing replaced. Post-repair: 1.8 mm/sec. | Ramesh Kumar | Ajay Mehta | SKF-6309-2RS x1, GKT-DN65-SW x2, MSHC100-500G x1 | 9 | 5500 | Cl. 5.2, 6.1 | CLOSED
WO-2024-0618 | 18-Jun-2024 | PUMP-102 | PM/CM | Planned shutdown: Mechanical seal replaced (dry-run damage per NMR-2024-0208), NDE bearing replaced. Wearing ring borderline. | Vikram Singh | Ajay Mehta | FSL-MX-DN65 x1, SKF-6306-2RS x1, MSHC100-500G x1 | 10 | 33050 | Cl. 6.3, 6.1 | CLOSED
INS-2024-Q3 | 22-Sep-2024 | PUMP-101, PUMP-102 | INSP | Q3 Running Inspection: all parameters satisfactory. PUMP-102 wearing ring at 0.48mm (borderline). Base plate corrosion noted. | Prasad Iyer | Ajay Mehta | None | 2 | 0 | Cl. 5.2, 6.1, 6.3 | CLOSED
WO-2024-1201 | 01-Dec-2024 | PUMP-101, PUMP-102 | PM | Q4 Planned PM: wearing ring replacement PUMP-102, lubrication both pumps, full inspection. | TBD | Ajay Mehta | WR-SS316-D65 x2, WR-SS316-D65-I x2, MSHC100-500G x2 | 8 | 18450 | Cl. 5.2, 6.1, 6.3 | PLANNED
SUMMARY
Total WOs
Total Cost (INR)
Total Downtime (hrs)

## Performance Monitoring
BHARAT STEEL PLANT – PUMP PERFORMANCE & VIBRATION MONITORING LOG
Pump House B ¦ Measurement Frequency: Monthly (Running Equipment Only) ¦ Instrument: Fluke 810 Vibration Analyser
Date | Equipment | Mode | Vibration DE (mm/sec) | Vibration NDE (mm/sec) | Bearing Temp DE (°C rise) | Bearing Temp NDE (°C rise) | Discharge Press. (bar) | Motor Current (A) | Remarks
10-Jan-2023 | PUMP-101 | DUTY | 1.9 | 1.7 | 12 | 13 | 6.7 | 11.1 | Normal. Post annual PM.
10-Jan-2023 | PUMP-102 | STANDBY | - | - | - | - | - | - | Standby – not running
10-Feb-2023 | PUMP-101 | DUTY | 2 | 1.8 | 13 | 14 | 6.8 | 11.3 | Normal
10-Mar-2023 | PUMP-101 | DUTY | 2.1 | 1.9 | 14 | 14 | 6.7 | 11.2 | Vibration slightly higher – monitor
10-Apr-2023 | PUMP-101 | DUTY | 2.3 | 2 | 14 | 15 | 6.6 | 11.4 | Vibration elevated. WO raised WO-2023-0601.
22-Jun-2023 | PUMP-101 | DUTY | 1.9 | 1.8 | 13 | 13 | 6.7 | 11.1 | Post impeller cleaning WO-2023-0622. Normal.
10-Jul-2023 | PUMP-101 | DUTY | 1.8 | 1.7 | 12 | 13 | 6.8 | 11 | Normal
10-Aug-2023 | PUMP-101 | DUTY | 1.9 | 1.8 | 13 | 13 | 6.7 | 11.1 | Normal
15-Sep-2023 | PUMP-101 | DUTY | 2 | 1.8 | 13 | 14 | 6.7 | 11.2 | Normal
10-Oct-2023 | PUMP-101 | DUTY | 2.1 | 1.9 | 13 | 14 | 6.8 | 11.3 | Normal
10-Nov-2023 | PUMP-101 | DUTY | 2.3 | 2.1 | 15 | 15 | 6.6 | 11.4 | Vibration trend increasing. Watch bearing.
10-Dec-2023 | PUMP-101 | DUTY | 2.5 | 2.2 | 16 | 16 | 6.5 | 11.5 | DE bearing wear suspected. Annual PM done.
10-Jan-2024 | PUMP-101 | DUTY | 3.1 | 2.4 | 17 | 16 | 6.4 | 11.7 | ⚠ DE vibration above 2.8 limit. WO raised.
10-Jan-2024 | PUMP-102 | DUTY | 1.8 | 1.7 | 12 | 12 | 6.8 | 11 | PUMP-102 switched to duty 12-Jan.
10-Feb-2024 | PUMP-101 | SHUTDOWN | - | - | - | - | - | - | Shutdown after vibration exceedance. Awaiting repair.
10-Feb-2024 | PUMP-102 | DUTY | 1.7 | 1.6 | 12 | 11 | 6.9 | 10.9 | Duty. Near-miss NMR-2024-0208 occurred 08-Feb.
12-Mar-2024 | PUMP-101 | DUTY | 1.8 | 1.7 | 14 | 13 | 6.8 | 11 | Post bearing replacement WO-2024-0312. Normal.
12-Mar-2024 | PUMP-102 | STANDBY | - | - | - | - | - | - | Standby. Seal leaking (3-5 drops/min). Scheduled repair.
10-Apr-2024 | PUMP-101 | DUTY | 1.7 | 1.6 | 13 | 13 | 6.9 | 10.9 | Normal
10-May-2024 | PUMP-101 | DUTY | 1.8 | 1.7 | 13 | 14 | 6.8 | 11 | Normal
18-Jun-2024 | PUMP-102 | DUTY | 1.6 | 1.5 | 11 | 12 | 6.9 | 10.8 | Post seal + NDE bearing replacement. Normal.
10-Jul-2024 | PUMP-101 | DUTY | 1.8 | 1.7 | 13 | 13 | 6.8 | 11.1 | Normal
10-Aug-2024 | PUMP-101 | DUTY | 1.8 | 1.8 | 14 | 13 | 6.7 | 11.2 | Normal
22-Sep-2024 | PUMP-101 | DUTY | 1.8 | 1.7 | 14 | 16 | 6.8 | 11.1 | Q3 Inspection. Normal.
22-Sep-2024 | PUMP-102 | STANDBY | 1.6 | 1.5 | 11 | 12 | - | - | Q3 Inspection. Wearing ring borderline 0.48mm.

## Equipment Register
BHARAT STEEL PLANT – EQUIPMENT REGISTER
Pump House B ¦ Centrifugal Pumps ¦ Maintained by: Mechanical Dept. ¦ Reviewed: Oct 2024
Equipment Tag | Description | Make | Model No. | Serial No. | Year Commissioned | Design Capacity (M³/Hr) | Rated Head (MLC) | Speed (RPM) | Motor Power (kW) | Current Status | Last Major Overhaul | Next PM Due
PUMP-101 | Single Stage Centrifugal Pump, End Suction, Back Pull-Out, SS304 | Kirloskar Brothers Ltd. | KBL-RD65-200 | KBL/2019/SP/4432 | 2019 | 30 | 70 | 2900 | 11 | DUTY | Dec 2023 | Dec 2024
PUMP-102 | Single Stage Centrifugal Pump, End Suction, Back Pull-Out, SS304 (Standby) | Kirloskar Brothers Ltd. | KBL-RD65-200 | KBL/2019/SP/4433 | 2019 | 30 | 70 | 2900 | 11 | STANDBY | Jun 2024 | Dec 2024
MTR-101 | 3-Phase Induction Motor – Duty for PUMP-101 | ABB | M2BAX-132M-2 | ABB/2019/MTR/7721 | 2019 | - | - | 2900 | 11 | DUTY | Dec 2023 | Dec 2024
MTR-102 | 3-Phase Induction Motor – Duty for PUMP-102 | ABB | M2BAX-132M-2 | ABB/2019/MTR/7722 | 2019 | - | - | 2900 | 11 | STANDBY | Jun 2024 | Dec 2024
VFD-101 | Variable Frequency Drive (VVVFD) for PUMP-101 | Siemens | SINAMICS G120 | SIE/2019/VFD/3301 | 2019 | - | - | - | 15 | OPERATIONAL | Jan 2023 | Jan 2025
VFD-102 | Variable Frequency Drive (VVVFD) for PUMP-102 | Siemens | SINAMICS G120 | SIE/2019/VFD/3302 | 2019 | - | - | - | 15 | OPERATIONAL | Jan 2023 | Jan 2025
TANK-201 | Feed Tank – SS304, 50 m³ capacity | Bharat Tanks Ltd. | BSP-T201-SS50 | BTL/2018/T/0981 | 2019 | - | - | - | - | OPERATIONAL | Mar 2024 | Mar 2025
STR-101 | Suction Strainer – Y-Type, SS316, DN80 | Forbes Marshall | YS-DN80-SS316 | FM/2019/STR/0441 | 2019 | - | - | - | - | OPERATIONAL | Apr 2022 | Apr 2025