BHARAT STEEL PLANT

Mechanical Maintenance Department

CORRECTIVE MAINTENANCE WORK ORDER

| WORK ORDER DETAILS |  |
| --- | --- |
| Work Order No. | WO-2024-0627 |
| Date of Issue | 27-June-2024 |
| Priority | CRITICAL — Production Impact |
| Work Order Type | Corrective Maintenance — Emergency Shutdown |
| Department | Utilities — Cooling Water System |
| EQUIPMENT DETAILS |  |
| Equipment Tag No. | HX-301 |
| Equipment Description | Shell & Tube Heat Exchanger — Cooling Water / Process Water Circuit |
| Manufacturer | Alfa Laval India Pvt. Ltd. |
| Model No. | AL-ST-DN200-16B |
| Serial No. | ALI/2018/HX/7741 |
| Design Pressure (Shell) | 10 bar |
| Design Pressure (Tube) | 6 bar |
| Design Temperature | Shell: 120°C ¦ Tube: 80°C |
| Operating Fluid (Shell) | Process Water (pH 7.5–9.0) |
| Operating Fluid (Tube) | Cooling Water (from Cooling Tower CT-101) |
| Location | Utilities Block C, Bay 2, Grid D-11 |
| PERSONNEL |  |
| Assigned Technician | Ramesh Kumar (Tech-ID: BSP-T-0045) |
| Supporting Technician | Vikram Singh (Tech-ID: BSP-T-0061) |
| Shift Engineer | Ajay Mehta (Shift Engineer – Mechanical) |
| Safety Officer | Sunil Patil |
| Permit to Work No. | PTW-2024-0934 (Hot Work + Confined Space) |

PROBLEM DESCRIPTION

At 09:45 hrs on 27-June-2024, the process water outlet temperature on HX-301 was observed to have risen to 74°C against a design limit of 55°C (as per OISD-117 Clause 8.1 — Heat Transfer Equipment Operating Limits). The DCS high-temperature alarm TAH-301 had activated at 08:30 hrs (set point: 60°C) but was initially acknowledged without investigation by the night shift operator. Continued rise in outlet temperature triggered an automatic process interlock shutdown of the downstream equipment at 09:45 hrs, resulting in a 3.5-hour unplanned production stoppage.

On initial inspection by Shift Engineer Ajay Mehta, the cooling water inlet flow to HX-301 was found significantly reduced — measured at 12 m³/hr against the design flow of 28 m³/hr. The shell-side differential pressure was elevated at 3.2 bar versus the normal 0.8 bar, strongly indicating tube-side fouling or blockage. Visual inspection of the cooling water outlet confirmed discolouration and suspended solids, consistent with biological fouling (bio-film growth) in the tube bundle.

ROOT CAUSE ANALYSIS (FISHBONE / 5-WHY)

| Why No. | Question | Finding |
| --- | --- | --- |
| Why 1 | Why did HX-301 overheat? | Reduced cooling water flow caused insufficient heat transfer, raising outlet temperature above design limit. |
| Why 2 | Why was cooling water flow reduced? | Tube bundle severely fouled with bio-film and mineral deposits — effective flow area reduced by ~55%. |
| Why 3 | Why did fouling accumulate to this extent? | Scheduled chemical cleaning (due March 2024) was deferred due to production pressure. Last cleaning performed: September 2023 — 9 months overdue. |
| Why 4 | Why was the deferral approved? | No formal risk assessment was conducted for the deferral. Approval was informal — no written record, no alternative monitoring plan put in place. |
| Why 5 | Why was no monitoring plan in place? | BSP maintenance procedure BSP-MP-HX-002 does not include a mandatory deferral protocol. Gap in procedure — no OISD-117 Clause 8.3 (Deferral of Statutory Maintenance) compliance check. |

WORK PERFORMED

| Step | Action | Detail |
| --- | --- | --- |
| 1 | Isolate HX-301 | Issued PTW-2024-0934 (Hot Work + Confined Space). Applied LOTO on shell-side and tube-side isolation valves (LOTO Tag: LOTO-0627-A/B). Confirmed zero pressure on both sides with pressure gauges. |
| 2 | Drain and Vent | Opened drain valves — shell-side drained 180 litres process water. Tube-side drained 95 litres cooling water. Vented both sides to atmosphere. Confirmed safe entry conditions per Factories Act 1948 Section 36 (Confined Space Entry). |
| 3 | Open Channel Covers | Removed front and rear channel covers (M24 bolts × 16 per cover). Gaskets found compressed and brittle — both replaced. |
| 4 | Tube Bundle Inspection | Inserted borescope into tube bundle — confirmed heavy bio-film fouling and calcium carbonate scale deposits in approximately 60% of tubes. 3 tubes found completely blocked. 2 tubes showing external pitting on shell side (depth < 0.5mm — within acceptable limit per IS 4503 Clause 6). |
| 5 | High Pressure Water Jetting | Cleaned all 186 tubes using high-pressure water jet (pressure: 350 bar) per IS 4503 and TEMA standards. Blockages in 3 tubes cleared successfully. Bio-film and scale deposits removed. Estimated 92% tube cleanliness achieved post-cleaning. |
| 6 | Chemical Passivation | Applied sodium hypochlorite solution (200 ppm) to tube-side for 2 hours to eliminate residual bio-film and inhibit regrowth. Flushed with clean water. Procedure per BSP-MP-HX-002 Clause 4.3. |
| 7 | Tube Integrity Test | Performed pneumatic test on tube bundle at 1.5× design pressure (9 bar) per IS 4503 Clause 7 and ASME Section VIII Div.1. Held for 30 minutes — no pressure drop detected. All tubes confirmed leak-free. |
| 8 | Gasket Replacement | Replaced all channel cover gaskets (Part No. GKT-DN200-GRAPH × 4 sets) with new spiral wound graphite gaskets per ANSI B16.20. |
| 9 | Reassembly | Reassembled channel covers. Torqued all M24 bolts to 220 Nm in cross-pattern sequence per Alfa Laval assembly procedure ALI-ST-ASM-Rev3. |
| 10 | Hydraulic Test | Filled shell and tube sides with water. Pressurised to 1.5× design pressure: shell side 15 bar, tube side 9 bar. Held 30 minutes each per IS 4503 Clause 7.2. No leakage detected. |
| 11 | Commission | Restored isolation valves. Opened cooling water slowly. Monitored outlet temperature — reached steady state at 48°C (within 55°C design limit) within 20 minutes. Differential pressure normalised to 0.9 bar. Production restart authorised at 13:20 hrs. |

KEY OBSERVATIONS

⚠ OBSERVATION 1 — Tube Pitting (Minor) Two tubes show external pitting on shell side (max depth 0.4 mm). Within IS 4503 allowable limit of 0.5 mm wall loss. Flagged for monitoring — if depth exceeds 0.5 mm at next inspection, tubes to be plugged per TEMA standards.

⚠ OBSERVATION 2 — Cooling Water Quality (Action Required) Cooling water from CT-101 shows elevated bacterial count (confirmed by water sample sent to BSP laboratory — results pending). Bio-film growth rate in HX-301 is likely accelerated by inadequate biocide dosing in cooling tower. Recommend immediate review of CT-101 water treatment programme per IS 10500 (Water Quality Standards) and OISD-117 Clause 8.4.

⚠ OBSERVATION 3 — Alarm Override (Safety Finding) TAH-301 alarm was acknowledged at 08:30 hrs without investigation. This is the second alarm-override incident in 2024 (ref: NMR-2024-0208 — PUMP-102 dry running incident). Pattern indicates systemic alarm management gap. Recommend mandatory alarm response training for all shift operators per OISD-GDN-206 Alarm Management Guidelines.

MATERIALS CONSUMED

| Part / Material | Part No. | Qty | Cost (INR) |
| --- | --- | --- | --- |
| Spiral Wound Gasket DN200 Graphite/SS316 | GKT-DN200-GRAPH | 4 Sets | ₹12,400 |
| Sodium Hypochlorite Solution 200 ppm | CHEM-NAOCL-200 | 50 Litres | ₹3,200 |
| PTFE Thread Seal Tape 25mm | SEAL-PTFE-25 | 4 Rolls | ₹320 |
| High Pressure Water Jetting Service (External) | SVC-HPWJ-HX301 | 1 Job | ₹45,000 |

REGULATORY & STANDARDS COMPLIANCE REFERENCES

| Regulation / Standard | Clause | Applicability to this Work Order |
| --- | --- | --- |
| OISD-117 | Clause 8.1, 8.3, 8.4 | Heat transfer equipment operating limits (8.1); deferral of statutory maintenance (8.3); cooling water quality requirements (8.4) |
| IS 4503 | Clause 6, 7, 7.2 | Shell and tube heat exchangers — design, manufacture, and testing standard. Tube wall loss limits (6); pressure test procedure (7, 7.2) |
| Factories Act 1948 | Section 36, Section 87 | Confined space entry requirements (Sec. 36); dangerous operations — mandatory written permit system (Sec. 87) |
| ASME Section VIII Div.1 | UG-99, UG-100 | Pressure vessel hydrostatic test (UG-99) and pneumatic test (UG-100) requirements — pressure at 1.5× MAWP |
| TEMA Standards | Class R, Section 6 | Tubular Exchanger Manufacturers Association — tube bundle cleaning procedures, fouling resistance values, tube plugging criteria |
| IS 10596 | General | Code of practice for selection, installation, operation and maintenance of industrial equipment — general maintenance discipline reference |
| IS 10500 | General | Drinking/process water quality standards — applicable to cooling water treatment and biocide dosing levels for CT-101 |
| OISD-GDN-206 | General | Alarm management guidelines — TAH-301 override incident to be reported and reviewed under this guideline |
| ANSI B16.20 | General | Ring-joint gaskets and grooves for steel pipe flanges — spiral wound gasket specification compliance |

CORRECTIVE ACTIONS & FOLLOW-UP

1. IMMEDIATE: CT-101 cooling water biocide dosing to be reviewed and corrected by Water Treatment team by 30-June-2024. Water sample results (BSP/LAB/2024/0627) to be reviewed when available.

2. SHORT TERM: BSP-MP-HX-002 to be revised to include mandatory deferral protocol per OISD-117 Clause 8.3 — any deferral of heat exchanger cleaning beyond 30 days requires written risk assessment and enhanced monitoring plan. Target: 15-July-2024.

3. SHORT TERM: TAH-301 alarm override event to be included in the alarm management review already initiated under NMR-2024-0208. Pattern of alarm overrides to be presented at next monthly safety meeting.

4. MEDIUM TERM: HX-301 tube pitting (2 tubes, max 0.4mm depth) to be re-measured at next planned inspection (December 2024). If depth exceeds 0.5mm, tubes to be plugged per TEMA Class R criteria.

5. LONG TERM: Evaluate installing online differential pressure monitoring (DPT-301) across HX-301 tube side with DCS alert at 1.5× normal DP — this would have given 48–72 hours advance warning of fouling progression. Target: Q1 2025 capital budget.

PRODUCTION IMPACT

| Parameter | Value |
| --- | --- |
| Unplanned Downtime | 3.5 hours (09:45 hrs – 13:20 hrs, 27-June-2024) |
| Estimated Production Loss | Approx. 42 MT process output — under assessment by Production Dept. |
| Total Maintenance Cost | ₹60,920 (parts + services) |
| Could Have Been Prevented? | YES — scheduled March 2024 cleaning would have prevented this incident |

| SIGN-OFF |  |
| --- | --- |
| Lead Technician | Ramesh Kumar ¦ 27-Jun-2024 ¦ 14:00 hrs |
| Supporting Technician | Vikram Singh ¦ 27-Jun-2024 ¦ 14:00 hrs |
| Shift Engineer Approval | Ajay Mehta ¦ 27-Jun-2024 ¦ 14:30 hrs |
| Safety Officer Review | Sunil Patil ¦ 28-Jun-2024 |
| Work Order Status | CLOSED |
| Next Scheduled Cleaning | December 2024 (6-month interval per revised BSP-MP-HX-002) |
| Next Tube Inspection | December 2024 (pitting monitoring) |