BHARAT STEEL PLANT

Inspection & Reliability Engineering Department

QUARTERLY PUMP INSPECTION REPORT – Q3 2024

| INSPECTION DETAILS |  |
| --- | --- |
| Report No. | INS-2024-Q3-PH-B |
| Inspection Date | 22-September-2024 |
| Inspector Name | Prasad Iyer (Reliability Engineer, Grade RE-II) |
| Inspection Standard | OISD-117 (Inspection of Rotating Machinery) ¦ IS 9137 (Testing of Centrifugal Pumps) |
| Equipment Covered | PUMP-101 ¦ PUMP-102 – Pump House B, Bay 3 |
| Inspection Type | Running Inspection (Equipment Online) |

INSPECTION CHECKLIST RESULTS

| Inspection Item | PUMP-101 Reading | P101 Status | PUMP-102 Reading | P102 Status |
| --- | --- | --- | --- | --- |
| Vibration (mm/sec) [Limit: 2.8] | 1.8 mm/sec | PASS | 1.6 mm/sec | PASS |
| Bearing Temp – DE (°C) [Limit: +20°C rise] | Amb+14°C | PASS | Amb+11°C | PASS |
| Bearing Temp – NDE (°C) | Amb+16°C | PASS | Amb+12°C | PASS |
| Mechanical Seal Leakage | Nil | PASS | Nil | PASS |
| Discharge Pressure (bar) | 6.8 bar | PASS | N/A (Standby) | PASS |
| Suction Pressure (bar) | 0.4 bar | PASS | N/A (Standby) | PASS |
| Motor Current (A) [FLA: 12.5A] | 11.2 A | PASS | N/A (Standby) | PASS |
| Noise Level (dB) [Limit: 85 dB] | 72 dB | PASS | N/A (Standby) | PASS |
| Coupling Guard Condition | Intact, secure | PASS | Intact, secure | PASS |
| Base Plate Condition | Minor corrosion, bay 3 drain blocked | WARN | Good | PASS |
| Wearing Ring Clearance | Not measured (running) | N/A | 0.48 mm (limit 0.5mm) | WARN |
| Seal Flush Line | Clear, flowing | PASS | Clear, flowing | PASS |
| LOTO Tags Visible | N/A (running) | N/A | LOTO applied – correct | PASS |

OBSERVATIONS & RECOMMENDATIONS

1. PUMP-101 operating within all parameters. Bearing temperatures stable since March 2024 repair (WO-2024-0312). Recommend continuing 3-monthly lubrication schedule.

2. PUMP-102 wearing ring clearance at 0.48 mm – borderline per OEM limit of 0.5 mm (noted in WO-2024-0618). Recommend measuring under next planned shutdown (December 2024). If clearance exceeds 0.5 mm at any point, pump should be removed from service for ring replacement.

3. PUMP-101 base plate – drain is blocked (debris accumulation). Minor surface corrosion on north face of base plate. Recommend cleaning drain and applying cold galvanising compound to corroded section before monsoon season (Oct 2024).

4. Lubrication history review: both pumps are now on 90-day greasing cycle per revised schedule (updated after NMR-2024-0208 review). Last lubrication: 01-Sep-2024 (Ramesh Kumar). Next due: 01-Dec-2024.

COMPLIANCE STATUS

Both PUMP-101 and PUMP-102 comply with OISD-117 Clause 5.2 (Vibration Limits for Rotating Machinery), Clause 6.1 (Temperature Monitoring), and Clause 6.3 (Seal Condition) as of inspection date. PUMP-102 wearing ring to be monitored at next shutdown. No regulatory non-conformances to report.

| SIGN-OFF |  |
| --- | --- |
| Inspector | Prasad Iyer ¦ 22-Sep-2024 |
| Shift Engineer Review | Ajay Mehta ¦ 23-Sep-2024 |
| Overall Status | SATISFACTORY – Minor observations noted |
| Next Inspection Due | December 2024 (Q4 Inspection) |