BHARAT STEEL PLANT

STANDARD OPERATING PROCEDURE

| SOP IDENTIFICATION |  |
| --- | --- |
| SOP Number | BSP-SOP-UTL-005 Rev.2 |
| Title | Operation of Centrifugal Pumps – Pump House B (PUMP-101 / PUMP-102) |
| Revision Date | 28-February-2024 |
| Previous Revision | Rev.1 – January 2021 |
| Reason for Revision | Updated following Near-Miss NMR-2024-0208 (Dry-running event PUMP-102). Added dry-running risk warnings and mandatory shutdown triggers. |
| Approved By | R.K. Sharma – AGM Mechanical ¦ Sunil Patil – Safety Officer |
| Applicable Equipment | PUMP-101 (Tag: PUMP-101) ¦ PUMP-102 (Tag: PUMP-102) – Single Stage Centrifugal Pumps, KBL RD65-200 |
| Applicable Regulations | OISD-117 ¦ IS 10596 ¦ Factories Act 1948 Sections 21, 22, 32 |

1. SCOPE

This SOP covers the safe start-up, normal operation, shutdown, and emergency shutdown of centrifugal pumps PUMP-101 and PUMP-102 in Pump House B, Bharat Steel Plant. All operators must read and understand this SOP before operating the pumps. Any deviation from this procedure requires written approval from the Shift Engineer.

2. HAZARDS & WARNINGS

⚠ WARNING – DRY RUNNING HAZARD (Updated per NMR-2024-0208) NEVER operate PUMP-101 or PUMP-102 when Feed Tank T-201 level is below 15% (1.2 m). Dry-running destroys the mechanical seal within 5–10 minutes of onset. Seal damage leads to process liquid leakage, creating a serious slip/chemical exposure hazard. If Low-Level Alarm LLA-201 activates: SHUT DOWN PUMP IMMEDIATELY. The DCS alarm override for LLA-201 now requires dual authorisation (Operator + Shift Supervisor). Overriding without authorisation is a Level 3 Safety Violation.

⚠ CAUTION – MECHANICAL HAZARD Never operate pump with coupling guard removed. Rotating coupling can cause severe injury. Ensure LOTO is applied before any maintenance activity. Pumps must not be run at zero flow (closed valve) for more than 30 seconds – risk of overheating pump casing.

3. PRE-START CHECKS

| Step | Action | Detail / Acceptance Criteria |
| --- | --- | --- |
| P1 | Check Tank T-201 Level | Verify DCS reading of LI-201 > 15% (1.2 m). Do NOT proceed if level is below 15%. |
| P2 | Inspect Pump Visually | Check for leakage at seal area, flange joints, and casing. Any active leakage – do not start. Inform supervisor. |
| P3 | Check Coupling Guard | Confirm coupling guard is fitted and all fasteners are tight. |
| P4 | Check Suction Valve | Ensure suction valve (SV-101/SV-102) is fully open before start. Never start with suction closed. |
| P5 | Check Discharge Valve | Keep discharge valve (DV-101/DV-102) slightly cracked open (10-15%) for starting. |
| P6 | Check Bearing Lubrication | Verify oil level in sight glass (for oil-lubricated bearings) or confirm last grease date from lubrication register (greasing interval: 90 days). |
| P7 | Check Seal Flush Line | Ensure seal flush line valve is open and line is clear. |
| P8 | Check Motor Isolation | Confirm motor is connected to power supply. Check MCC indication for healthy status. |

4. START-UP PROCEDURE

| Step | Action | Detail |
| --- | --- | --- |
| S1 | Start Motor from MCC/DCS | Press START on local panel or initiate from DCS workstation. Motor should reach full speed within 5 seconds. |
| S2 | Open Discharge Valve Slowly | Gradually open DV-101/DV-102 over 15–20 seconds to avoid water hammer. |
| S3 | Check Discharge Pressure | Discharge pressure should read 6.5–7.0 bar on PI-101/PI-102 within 30 seconds of start. |
| S4 | Check Motor Current | Full Load Ampere: 12.5A. Acceptable running range: 10–13A. If current exceeds 13A, shut down and investigate. |
| S5 | Check for Vibration | After 2 minutes of running, manually check for unusual vibration. Acceptable limit: 2.8 mm/sec. Shut down if vibration is noticeably abnormal. |
| S6 | Check for Seal Leakage | No drips acceptable. Minor seepage (1 drop/min) – log and monitor. More than 3 drops/min – shut down. |
| S7 | Log Start in Shift Register | Record start time, pre-start checks confirmed, and initial readings in Pump House B Shift Register. |

5. NORMAL SHUTDOWN PROCEDURE

| Step | Action | Detail |
| --- | --- | --- |
| N1 | Throttle Discharge Valve | Partially close DV to reduce flow before stopping motor. |
| N2 | Stop Motor | Press STOP at MCC or DCS. Motor should decelerate to full stop within 15 seconds. |
| N3 | Close Discharge Valve | Fully close DV-101/DV-102 after motor stops to prevent back-flow. |
| N4 | Log Shutdown | Record stop time and reason in Shift Register. |

6. EMERGENCY SHUTDOWN PROCEDURE

Initiate emergency shutdown IMMEDIATELY if any of the following conditions occur:

• LLA-201 Low-Level Alarm activates (Tank T-201 below 15%)

• Vibration exceeds 4.5 mm/sec (trip level)

• Bearing temperature rise exceeds 35°C above ambient

• Seal leakage exceeds 3 drops/minute

• Any abnormal noise, smoke, or burning smell from motor or pump

• Any personnel injury in proximity to the pump

Action: Press RED EMERGENCY STOP button on local panel. Do not attempt to restart without Shift Engineer authorisation. Inform safety officer immediately.

| DOCUMENT CONTROL |  |
| --- | --- |
| Prepared By | Process Engineering Dept. – D. Rao |
| Reviewed By | R.K. Sharma (AGM Mechanical) |
| Approved By | Sunil Patil (Safety Officer) |
| Next Review Due | February 2025 (Annual Review per BSP-QMS-DCR-001) |