BHARAT STEEL PLANT

Mechanical Maintenance Department

MAINTENANCE WORK ORDER

| WORK ORDER DETAILS |  |
| --- | --- |
| Work Order No. | WO-2024-0312 |
| Date of Issue | 12-March-2024 |
| Priority | HIGH |
| Work Order Type | Corrective Maintenance |
| Department | Utilities – Pump House B |
| EQUIPMENT DETAILS |  |
| Equipment Tag No. | PUMP-101 |
| Equipment Description | Single Stage Centrifugal Pump – SS304 |
| Manufacturer | Kirloskar Brothers Limited |
| Model No. | KBL-RD65-200 |
| Serial No. | KBL/2019/SP/4432 |
| Rated Capacity | 30 M³/Hr |
| Rated Head | 70 MLC |
| Operating Speed | 2900 RPM |
| Location | Pump House B, Bay 3, Grid F-7 |
| PERSONNEL |  |
| Assigned Technician | Ramesh Kumar (Tech-ID: BSP-T-0045) |
| Supervisor | Ajay Mehta (Shift Engineer – Mechanical) |
| Safety Officer | Sunil Patil |

PROBLEM DESCRIPTION

Excessive vibration detected on PUMP-101 during routine shift inspection at 06:30 hrs. Vibration level measured at 6.2 mm/sec (limit: 2.8 mm/sec as per IS 2372). Abnormal noise from bearing housing also reported by operator Mohan Das. Pump was placed on standby and PUMP-102 switched to duty mode.

WORK PERFORMED

1. Issued Permit to Work No. PTW-2024-0445 (Cold Work) before commencing.

2. Isolated pump from electrical supply (LOTO applied – Tag No. LOTO-0312-A).

3. Disconnected suction and discharge flanges. Drained pump casing.

4. Removed coupling guard and flexible coupling (Bibby type, Grid coupling).

5. Extracted bearing housing cover – found DE (Drive End) bearing severely pitted and cage fractured. Bearing Part No.: SKF-6309-2RS.

6. Replaced DE bearing with new SKF-6309-2RS (Batch: SKF/2023/Q4). Applied specified bearing grease (Mobil SHC 100).

7. Inspected NDE (Non-Drive End) bearing – found acceptable, minor wear. Left in service; flagged for replacement at next PM.

8. Checked mechanical seal – no leakage observed. Seal in acceptable condition.

9. Reassembled pump. Realigned pump-motor assembly using dial gauge. Final TIR reading: 0.03 mm (within 0.05 mm limit per spec).

10. Commissioned pump. Vibration post-repair: 1.8 mm/sec. Normal operation confirmed.

MATERIALS CONSUMED

| Part Name | Part No. | Qty | Source |
| --- | --- | --- | --- |
| SKF Deep Groove Bearing 6309-2RS | SKF-6309-2RS | 1 No. | Stores – BSP/STR |
| Bearing Grease – Mobil SHC 100 | MSHC100-500G | 1 Cartridge | Stores – BSP/STR |
| Gasket – DN65 Spiral Wound | GKT-DN65-SS | 2 Nos. | Stores – BSP/STR |

COMPLIANCE REFERENCE

Maintenance performed as per OISD-117 (Inspection of Rotating Equipment), IS 10596 (Installation and Maintenance of Pumps), and BSP Internal Maintenance Procedure BSP-MP-004 Rev.2.

RECOMMENDATIONS

1. Schedule replacement of NDE bearing at next planned shutdown (estimated: June 2024).

2. Investigate root cause of premature bearing failure – bearing was replaced only 14 months ago. Suspected cause: lubrication interval exceeded.

3. Review lubrication schedule for all Pump House B equipment against OISD-117 requirements.

| SIGN-OFF |  |
| --- | --- |
| Technician Signature | Ramesh Kumar ¦ 12-Mar-2024 ¦ 15:45 hrs |
| Supervisor Approval | Ajay Mehta ¦ 12-Mar-2024 ¦ 16:10 hrs |
| Work Order Status | CLOSED |
| Next PM Due | June 2024 (Planned Shutdown) |