BHARAT STEEL PLANT

Mechanical Maintenance Department

MAINTENANCE WORK ORDER

| WORK ORDER DETAILS |  |
| --- | --- |
| Work Order No. | WO-2024-0618 |
| Date of Issue | 18-June-2024 |
| Priority | MEDIUM |
| Work Order Type | Planned Preventive Maintenance |
| Department | Utilities – Pump House B |
| EQUIPMENT DETAILS |  |
| Equipment Tag No. | PUMP-102 |
| Equipment Description | Single Stage Centrifugal Pump – SS304 (Standby Unit) |
| Manufacturer | Kirloskar Brothers Limited |
| Model No. | KBL-RD65-200 |
| Serial No. | KBL/2019/SP/4433 |
| Rated Capacity | 30 M³/Hr |
| Rated Head | 70 MLC |
| Location | Pump House B, Bay 3, Grid F-8 |
| PERSONNEL |  |
| Assigned Technician | Vikram Singh (Tech-ID: BSP-T-0061) |
| Supervisor | Ajay Mehta (Shift Engineer – Mechanical) |
| Safety Officer | Dinesh Rao |

SCOPE OF WORK

Planned Preventive Maintenance during June 2024 shutdown window. PUMP-102 was identified during WO-2024-0312 as having a leaking mechanical seal (minor weeping observed at seal face – approx. 3–5 drops/minute). This work order addresses the deferred mechanical seal replacement and the NDE bearing replacement flagged in WO-2024-0312.

WORK PERFORMED

1. Issued Permit to Work No. PTW-2024-0891 (Cold Work) before commencing.

2. De-energised and LOTO applied (Tag: LOTO-0618-B). Drain valve opened, casing drained fully.

3. Removed coupling guard, coupling, and bearing housing cover.

4. Extracted impeller and shaft assembly (back pull-out design – no pipe dismantling required).

5. Removed old mechanical seal (Type: Single, Unbalanced Cartridge, SiC/SiC faces). Faces showed heat discolouration and micro-cracking on rotary face – indicative of dry-running event.

6. Fitted new mechanical seal – Flowserve Type MX Single Cartridge Seal, SiC/SiC faces, Teflon secondary seal. Fitted per manufacturer procedure FSL-MX-INST-Rev4.

7. Replaced NDE bearing (SKF-6306-2RS) as flagged in WO-2024-0312.

8. Inspected wearing rings – clearance measured at 0.48 mm (limit: 0.5 mm per OEM spec). Left in service; borderline, flagged for next inspection.

9. Reassembled pump. Alignment check performed: TIR = 0.04 mm (within limit).

10. Pump commissioned and run for 2 hours. No seal leakage. Vibration: 1.6 mm/sec. Bearing temperature: 42°C (ambient 31°C, rise 11°C – within 20°C grease limit).

ROOT CAUSE NOTE – DRY RUNNING

Dry-running of the mechanical seal is suspected to have occurred on 08-Feb-2024 when a tank low-level alarm was overridden by the night shift operator (see Near-Miss Report NMR-2024-0208). This incident caused premature seal face damage. Corrective action: Low-level interlock override now requires dual authorisation per BSP-SOP-UTL-007 Rev.1.

MATERIALS CONSUMED

| Part Name | Part No. | Qty | Cost (INR) |
| --- | --- | --- | --- |
| Flowserve MX Cartridge Seal SiC/SiC | FSL-MX-DN65 | 1 No. | ₹28,500 |
| SKF Bearing 6306-2RS (NDE) | SKF-6306-2RS | 1 No. | ₹3,200 |
| Bearing Grease Mobil SHC 100 | MSHC100-500G | 1 Cartridge | ₹850 |

COMPLIANCE REFERENCE

Work performed as per OISD-117 Clause 6.3 (Mechanical Seals – Inspection and Replacement Criteria), IS 10596, Flowserve Installation Procedure FSL-MX-INST-Rev4, and BSP Maintenance Procedure BSP-MP-004 Rev.2.

| SIGN-OFF |  |
| --- | --- |
| Technician Signature | Vikram Singh ¦ 18-Jun-2024 ¦ 14:20 hrs |
| Supervisor Approval | Ajay Mehta ¦ 18-Jun-2024 ¦ 15:00 hrs |
| Work Order Status | CLOSED |
| Next PM Due | December 2024 |